## Slide 1: MERSIM Module of WASP-IV
Mladen Zeljko, Ph.D.
Head of Energy Generation and Conversion Department
Energy Institute “Hrvoje Požar”
Tel: +385 1 6326186 Fax: +385 1 6040599
E-mail: mzeljko@eihp.hr
www.eihp.hr

## Slide 2: Introduction to MERSIM Module
1. Simulates system operation for each configuration (state) and for each period in the year and each hydrological condition (merge and simulates)

## Slide 3: Introduction to MERSIM Module
2. MERSIM determines:
  Energy generated by each generating unit in each period
  Capacity factors
  Fuel costs
  Operation and maintenance costs
  LOLP (with maintenance)
  Energy not served

## Slide 4: Introduction to MERSIM Module
3. Methodology Used:
  Loading Order
  Spinning Reserve
  Probabilistic Simulation
  Saves previous calculations

## Slide 5: Inputs to MERSIM Module
Output Option
Loading Order
Spinning reserve criteria
Number of Fourier Coefficients to be used for simulation
Energy limit by fuel type
Fuel consumption by unit
Fuel stock by unit

## Slide 6: Calculating Loading Order in MERSIM
1. CASE A (Fixed L.O.)
  User Specifies Loading Order, both for Base and Peak Portions
  Spinning Reserve is not considered

## Slide 7: Calculating Loading Order in MERSIM
2. CASE B
  L.O. calculated by MERSIM to meet a specified spinning reserve criterion which is given by the user as a function of the largest unit block already loaded and the period peak load
  User specifies a basic economic loading order, which MERSIM tries to respect and still satisfy reserve criterion

## Slide 8: Calculating Loading Order in MERSIM
3. CASE C
  Same as Case B before, but spinning reserve is a constant value

## Slide 9: Loading Order In MERSIM 1. Case A
User specifies both base and peak portion in L.O.
  Base-load portion indicated by the number of corresponding plant from combined list of FIXSYS + VARSYS (Note: Thermal plants in FIXSYS begin with number 3, VARSYS plant numbers begin with number of last FIXSYS plant plus 1)

## Slide 10: Loading Order In MERSIM 1. Case A (cont’d)
  Peak load portion is indicated by adding 1000 to the number of base load portion
  If MWC = MWB (a single block unit), only base load portion number appears
  Hydro plants automatically handled by the program (numbers 1 and 2)

## Slide 11: Loading Order In MERSIM 2. Case B
L.O. calculated by MERSIM to satisfy spinning reserve requirements
  Spinning Reserve (S.R.) value given by equation:
  S.R. = A x (Largest Capacity Block Already Loaded) +
  + B x (Period Peak Load)
  where A, B, are coefficients and 0<A<5
  Basic loading order given by user or passed by CONGEN (but plants are represented by a single number and not base and peak as in case A)
  Hydro plants are handled automatically

## Slide 12: Loading Order In MERSIM 3. Case C
Same as Case B, but Spinning Reserve is a constant value (in MW)
  Basic loading order given by user or passed by CONGEN (as in case B)
  Hydro plants are handled automatically

## Slide 13: MERSIM Output
MERSIM can produce three levels of output (printout options):
  Minimum
  Intermediate
  Maximum
It can also print FIXSYS and VARSYS input files

## Slide 14: MERSIM Output
Minimum output
List of configurations with total operation cost
Expected average annual LOLP with and without maintenance
Energy not served for each hydro condition

## Slide 15: MERSIM Output
Intermediate output
Minimum Output
Summary of annual costs (fuel and O&M) by thermal “fuel” plant type for each hydro condition

## Slide 16: MERSIM Output
Maximum output
Intermediate Output
Detailed Loading Order calculations and results of simulations for each configuration, per period and hydro condition

## Slide 17: Simplified Illustration of Treatment of Forced Outages
1
2
3
4
5
6
7
8
9
UNIT 1
(20% FORCED OUTAGE RATE)
q1 = 0.2
p1 = 0.8
{
MW1
LOAD CURVE AS SEEN
BY UNITS 2-9 WHEN
UNIT 1 IS UNAVAILABLE
(20% OF TIME)
}
F(y - MW1)
EQUIVALENT LOAD CURVE
WHEN OUTAGES OF
UNIT 1 ARE INCLUDED
}
BASIC LOAD CURVE WHEN
UNIT 1 IS AVAILABLE
(80% OF TIME)
y = f(x)
x = f(y)
MW
X TIME
y = f(x) LOAD CURVE
x = f(y) INVERTED LOAD CURVE

## Slide 18: Ultimate Equivalent Load Duration Curve
MW
Time (fraction)
INSTALLED CAPACITY
MINIMUM
LOAD
PEAK LOAD
UNRELIABLE
CAPACITY
BASIC LOAD DURATION CURVE
ULTIMATE EQUIVALENT LOAD
DURATION CURVE
LOSS-OF-LOAD-PROBABILITY (LOLP)
ENERGY NOT SERVED (ENS)
LOLP

## Slide 19: Analysis of MERSIM Output
1. Capacity Factors
  Should not be greater than 100%
  Peaking units should not have high CFs
  Base load units should not have low CFs (unless out for maintenance in period

## Slide 20: Analysis of MERSIM Output
2. Energy Balance
  Is equal to total generation plus unserved energy minus energy under LDC
  Indication of accuracy of simulation
  Should be a small number

## Slide 21: Analysis of MERSIM Output
3. Number of Fourier Coefficients
  Plot values of ENS and LOLP using 10, 20, and 30 coefficients
  Keep track of time needed for each run