## Slide 1: LOADSY Module of WASP-IV
Mladen Zeljko, Ph.D.
Head of Energy Generation and Conversion Department
Energy Institute “Hrvoje Požar”
Tel: +385 1 6326186 Fax: +385 1 6040599
E-mail: mzeljko@eihp.hr
www.eihp.hr

## Slide 2: Key Inputs to LOADSY
Number of periods per year with a maximum of 12 periods
Number of cosine terms to be used in the fourier approximation to the inverted LDC
  maximum: 100
  “recommended: 50”

## Slide 3: Load duration curve

## Slide 4: Chronological Hourly Loads are the Starting Point for Preparing the Input Data for LOADSY
Peak Load
Minimum Load

## Slide 5: In the Next Step, the Hourly Loads are Sorted and Displayed in a Load Duration Curve
Peak Load
Minimum Load

## Slide 6: In the Final Step, the Load Duration Curve is Normalized
Minimum Load

## Slide 7: How to get hourly load data for the whole planning period?
The most simple way is to use load pattern from the past and multiply it with some annual growth rate.
Recommendation : use MAED (Model for the Analysis of Energy Demand) or similar model which can analise structure of energy demand.

## Slide 8: MAED Model
INPUT
Energy sector data (energy balance)
Scenario assumptions
  Socio-economic
  Technological
Substitutable energy uses
Process efficiencies
Hourly load characteristics
MAED
OUTPUT
Final energy demand
Electricity demand
Hourly electric load
Load duration curves (ELECTRIC)
MAED is a model relating the energy demand to the set of social, economic and technological factors that influence this demand.

## Slide 9: LDC Approximation
Need for matematical aproximation of LDC
Two possibilities in WASP
- by Fourier series, or
- by fifth - order polinomial

## Slide 10: Fourier Series LDC Approximation

## Slide 11: Approximation of LDC with a Fifth-Order Polynomial
f(x) = a0 + a1x + a2x2 + a3x3 + a4x4 + a5x5
f(x) defined in the interval [0, 1]
Necessary conditions:
f(0) = a0 = 1.0
  Pmax = 1.0
  f(1) = Pmin/Pmax)
  area under curve must equal the energy in the period
  f(x)dx = Load Factor LF

## Slide 12: Key Inputs to LOADSY (cont’d)
Annual peak loads in MWe for a maximum of 30 years
Period peak load ratios for each year of the study
  ratio of period peak load to annual peak
  at least one ratio in each year must be 1.0

## Slide 13: Key Inputs to LOADSY (cont’d)
Load duration curves expressed as either
  fifth-order polynomial with a constant coefficient of 1.0
  point-by-point description which gives better fitting of the Fourier expansion of the load duration curve (maximum of 100 points per LDC)

## Slide 14: Loadsy.dat
Case B11 - pump storage, additional peak import
12 100 0
717.2 2002
2
0.953 0.943 0.848 0.722 0.517 0.523 0.502 0.484 0.628 0.760
0.930 1.000
4
12
60
1.0000 0.0000
0.9731 0.0169
0.9464 0.0339
0.9386 0.0508
0.9301 0.0678
0.9229 0.0847
…………………
…………………
0.4573 1.0000

## Slide 15: Loadsy.dat
1
755.0 2003
1
792.7 2004
1
830.4 2005
2
0.994 0.957 0.826 0.742 0.591 0.589 0.564 0.506 0.678 0.779
0.918 1.000
4
12
60
1.0000 0.0000
0.9540 0.0169
…………………
…………………
0.5124 1.0000
1
862.3 2006
…………………
…………………
1204.6 2015
1

## Slide 16: Example for Period Peak Load Ratios to Annual Peak Load